## Slide 1: Opening Pandora’s Box Evaluating the Integrity of Water System Monitoring Nancy Feagin, P.E. and Steve Deem, P.E. Office of Drinking Water Washington State Department of Health ASDWA Webinar January 2017

## Slide 2: Office of Drinking Water’s Mission
We work with others to protect the health of the people of Washington State by ensuring safe and reliable drinking water.

## Slide 4: Enhance public health protection by optimizing the performance and operations of existing facilities
EPA Data Integrity Workshops 2012-2015
Turbidity Data Integrity Project (2012-2013)
  25 systems NW Region
  Continuing follow-up across the state

## Slide 6: Disinfection Data Integrity Project
33 Surface Water treatment plants in NW region
Diverse treatment technologies
  Unfiltered
  Membrane, bag, slow sand
  UV
  Ozone
  Primary disinfection: free Cl2
  Huge range in system size (1 gpm to 180 MGD)
  Learn-as-you-go, adaptive approach
  CT Requirements – DOH file review
  Operator interview (SOPs, maintenance, reporting)
  Portable testing equipment

## Slide 7: Accuracy and Precision
Accuracy is the closeness of a measured value to a standard or known value.
  You measure 5 kg for a 10 kg weight – not accurate.
Precision is the closeness of two or more measurements to each other. (Consistency)
  If you measure 5 kg three time in a row – you are precise (just not accurate!)
Accuracy and Precision are independent of each other.

## Slide 8: What is Data Integrity?
Maintaining and ensuring accuracy and consistency of data from sample collection point until the data is used.
Instrument selection, maintenance and calibration
Replaceable parts (photocells, sample lines, bulbs)
Human factors

## Slide 9: Disinfection Barrier – Killing Microbes
Disinfection goal – kill or prevent infectious microbes (virus, bacteria, protozoa) from replicating (inactivate).
More powerful the disinfectant – the less time the disinfectant needs to inactivate the bug.
Disinfectant may physically destroy or damage the organism – oxidize protein coat
Disinfectant may disrupt DNA – UV light

## Slide 10: Disinfection Monitoring
Much more complex than turbidity!
  Three water quality parameters:
    pH
    temperature
    disinfectant residual concentration
  PLUS . . .
pH
  Time =
Effective volume

## Slide 11: pH
Ways to measure pH
  Indicators – materials designed to change color at different pH values.
  Colorimeter – reagent added to sample vial, compare resultant color to wheel or spectral standard to interpolate pH.
  pH meter – potentiometric measurement using glass electrode and reference electrode. Precise and Continuous.
Soren Peder Lauritz Sorenson – 1909 - Danish - Carlsburg Laboratory
  Soren measured mV in solutions of known HCl concentration

## Slide 12: pH
A measurement of
  the hydrogen ion concentration [H+]
  the relative acidity of an aqueous solution
A negative logarithmic function pH = -log [H+]
Each one-unit decrease in pH = 10x increase in acidity: for example, a pH 6 solution 10 times more acidic than a pH 7 solution
What does the ‘p’ in pH stand for?
  Derived from Potenz – german for power or exponent – “power or potential of hydrogen”

## Slide 13: Chlorine Effectiveness and pH
Hypochlorous acid: a stronger disinfectant
Hypochlorite ion: A weaker disinfectant
http://www.hach.com/DisinfectionSeries02
HOCl  H+ + OCl-
At 20C

## Slide 14: Giardia Inactivation by Cl2 sensitivity to pH
Example:
Direct filtration plant
1 log Giardia Inactivation
Temp = 7° C
Cl2 = 1.1 mg/L
pH = 7.6
Need 58 minutes
pH
If your pH measurement is low, you will under-estimate how much time you need.
0.5 pH units = 17% error
true value
measured

## Slide 15: pH Meter Quiz: According to Standard Methods, when should you calibrate a bench top pH meter?
A. Before every measurement
B. Once a day
C. Once a month
D. Not needed

## Slide 16: Analytical Methods: pH
Standard Methods 4500 H+
EPA Method 150.1 and 150.2 (online)
New! EPA Method 150.3
ASTM D1293

## Slide 17: Project Findings: pH
Unapproved equipment (pool style)
Lack of daily calibration: 5/32 never calibrate
5/27 only use one buffer
No SOPs
Aerated sample
Low ionic strength water (<100 µS/cm) needs special probe, hard to consistently measure
Continuous: outdated 1982 method & lack of calibration guidance from manufacturer
  EPA updated method (82 FR 34861, published 7-27-2017)

## Slide 18: Trouble with pH
Most difficult to measure
Sensitive to time, temperature, sample collection (aeration), probe care and maintenance, calibration, verification …
Differences in accepted practice (transporting the sample, swirl, stirred, quiescent, calibrate, verify, one buffer, two
Measure in the field
Use consistent procedures
Allow probe to stabilize on both temp and pH
Calibrate minimum 2 buffers (bracket)
Verify with a different buffer

## Slide 19
Setup for Easy Maintenance (design by Shane King)

## Slide 20: Giardia Inactivation by Cl2 sensitivity to temperature
Same example:
Direct filtration plant
1 log Giardia Inactivation
Temp = 7° C
Cl2 = 1.1 mg/L
pH = 7.6
Need 58 minutes
If your temperature measurement is high, you will under-estimate how much time you need.
2˚C = 14% error
Temp (C)
true value
measured

## Slide 21: Temperature Quiz: How accurate should your thermometer be?
A. +/- 0.20 C
B. +/- 0.40 C
C. +/- 1.00 C
D. +/- 2.00 C

## Slide 22: Analytical Methods: temperature
Standard Methods 2550 (22nd Ed)
  Any standard liquid-in-glass or electronic thermometer
  Able to detect temp changes of 0.1 C or less
  +/- 0.4 C accuracy
  Periodically check against NIST-certified precision thermometer (e.g. 1-2 x/year)

## Slide 23: Project Findings: temperature
Questionable equipment: 28/33
No verification: 28/33
Plant thermometer: Only marked in 1F increments… reading six degrees low!

## Slide 24: Analytical Methods: chlorine residual
Standard Methods 4500 series!
  Cl D Amperometric Titration
  Cl F Ferrous Titrimetric Method
  Cl G DPD Colorimetric (N,N-diethyl-p-phenylenediamine)
  Cl H Syringaldazine

## Slide 25: Project Findings: Cl2 residual
Grab sampling:
Unapproved equipment or method: color wheel, pool test kit (11/33)
  No verification (9/11)
Expired reagents (2/33)

## Slide 26
Drinking Water Staff Cl2 Test Method Challenge

## Slide 27: Troubles with Measuring Cl2 Residual Grab Samples
Wrong vial (high range)
Cap off
Low/high range setting
Time
Mixing: Swirl versus shake
Wet vial
Condensation
Stained vial
Scratched vial
No free chlorine (ammonia?)

## Slide 28: Online Chlorine Analyzers
Colorimetric | Amperometric (electrochemical)
Intensity of color from reaction of chlorine with DPD indicator. The deeper the color, the higher the chlorine concentration. | Electrical current generated by reaction of chlorine with electrodes. The larger the current, the higher the chlorine concentration.
Pros Factory calibrated (verification only) Independent of changes in sample pH, temperature, chlorine concentration Only EPA-approved online method (without method 334.0) | Pros Fast response (continuous) Reagentless No waste stream Low maintenance: membrane/electrolyte every 3-6 mo
Cons Slower response (batch process) Reagents (monthly change) waste stream management Tubing replacement every 6 months | Cons Greater sensitivity to changes in sample pH, temperature, flow, pressure, chlorine Fouling by Fe/Mn Must calibrate by comparison with portable or lab instrument Must follow method 334.0

## Slide 29: Amperometric Analyzers EPA Method 334.0
A performance-based method
Allows any on-line chlorine analyzer
Requires a grab sample reference method
Requires proof of performance and routine QC for:
  Grab sample method
  Sample collector
  Online analyzer
IDC - Initial Demonstration of Capability. Initial verification of accuracy & precision of a grab sample method, sample collector and/or online analyzer.

## Slide 30: Project Findings: Cl2 residual
Continuous/On-line Analyzers: 15 Systems
Inadequate maintenance/setup (Cl-17) 6/11 (55%)
Not verifying every 5 days - 11 / 15 (73%)
Inadequate sample flow (Cl-17) - 8/11 (73%)

## Slide 31: HACH Cl-17
Colorimetric-intensity of light passing through a colored sample
Factory-programmed calibration converts absorbance into mg/L chlorine residual
Batch mode (2.5 minute cycle)
A two-step process: ZERO then READ
Range 0-5 mg/L
Signal averaging: four options
  Option 4: highest of last 2 readings

## Slide 32: HACH Cl-17 sample flow
Specifications: 200-500 mL/min
“Ideal” = 300 mL/min
Low flow causes low readings due to incomplete cell flushing
High flow causes low readings due to constant flushing
How to measure:
  From the drain during the 30 second flush (pink color)
  Multiply by 2 to get mL/min

## Slide 33: Hach Cl-17 setup & maintenance in the manual
Needs constant head 24 inches above the box
Change buffer/reagents monthly
Replace internal tubing every 6 months
Replace external tubing every 12 months

## Slide 34: Don’t Forget Maintenance!
Post maintenance tasks & instructions on the instrument
Tubing Replacement Interval:
Four years

## Slide 35: Online Analyzer Quiz: How often should you verify the online instrument to a benchtop chlorine test unit?
A. Daily
B. Twice a week
C. Every 5 days
D. Monthly
C. Never

## Slide 36: Peak Hourly Flow (PHF)
Measured directly (flow meter) (14/33)
Estimated using daily plant production (7/33)
Estimated from historical meter readings
Assumed constant using engineering calculations
We’ve always done it that way (no idea why)
  12/33 use assumed values
No routine WTP or PHF meter verification (28/33)
Direct measurement of peak hourly flow with a calibrated flowmeter is best

## Slide 37: Project Findings-Contact Volume
Physical Dimensions
  18/33 (54%) not verify dimensions
  5/11 don’t match calculations
Volume/Water Level
27 Systems use storage tanks / clearwells for CT
Don’t record water level – 13/27
Can’t (easily) measure
  Five systems had no level measuring devices
Operator unaware of minimum depth assumption

## Slide 38: Project Findings-Contact Volume
Physical Dimensions:
Calculations assume 50,000 gal
Measured Volume: 44,600 gal
  11% error
Assumed Minimum Water Level:
Calculations assume tank is full (15 ft)
Actual water depth=11 feet: 32,700 gal
  35 % less total volume than we thought!

## Slide 39: Baffling Efficiency (BE) aka T10/T higher BE means less short circuiting
None

## Slide 40: Findings-Baffling Efficiency
Unbaffled tank (Assigned BE = 0.3)
Baffled tank? (Assigned BE = 0.7)
?
9/27 contact tank BE > 0.1
8/9 not verified by tracer study – assumed values
5/7 w/ internal baffles not Inspected

## Slide 41: Other Findings: Inappropriate sample locations
A
B
B
A
Cl2
Cl2
  pH/temp: 12/33
  chlorine residual: 3/32

## Slide 42
A
B
C
D
A – filtered water entering clearwell; B – chlorine injection point;
C – pH adjustment; D – pump wet well (4 finished water pumps)

## Slide 43: Other Findings: Monitoring/Reporting
Not calculating inactivation ratio daily: 6/33
No Standard Operating Procedures (SOPs): 30/33

## Slide 44: Standard Operating Procedures (SOPs)
A tool to ensure that everyone does it the right way every time. They need to be:
Written down
Up-to-date
Consistent with industry best practices
Aligned with regulatory requirements

## Slide 45: Standard Operating Procedures (SOPs)
Can be as simple as you want
Make sure it works-have someone read it and perform the task (new employee?)
Keep a revision date on each SOP
Review periodically (annual preferred for critical activities & processes)

## Slide 46: Ddip- Number of Issues Observed
Issues that could impact data accuracy and precision were found at every plant
One system had only 2 issues, all the rest had more
Eleven systems had at least 9 separate issues
The average across all 33 plants was eight issues

## Slide 47: So What Difference Does it Make Quiz: Which parameter produced the greatest percent error in the disinfection inactivation ratio (IR)?
A. Contact time
B. Temperature
C. pH
D. Chlorine residual
How great was the error?
183%
39%
38%
19%

## Slide 48: dDIP Follow-up: Tracer Study Project
Goal: confirm unverified baffling factors (T10/T)
Selection criteria:
  Empirical baffling 0.3 or greater, OR
  Previous tracer issues (tracer or flow interruptions, single flow)
39 systems identified statewide, 32 participated
Funded by SRF setaside
April 2016 - June 2017

## Slide 49: Overall results: assumed T10/T values too high
5 were better than assumed
3 were equal to assumed
18 were worse than assumed
6 were better than assumed
5 were equal to assumed
20 were worse than assumed

## Slide 50: Surprises: unequal flow splitting
Basin construction same  poor flow splitting
T10 values vastly different 38 minutes versus 73 minutes
34%:66% flow splitting assuming similar BE

## Slide 51: Surprises: Coiled pipe inside storage reservoir used for CT T10/T=1.0 in pipe
Outlet Pipe
Inlet Pipe
18” Corrugated CT Piping Inside Reservoir
Coiled pipe inside storage reservoir used for CT T10/T=1.0 in pipe.

## Slide 52: Baffled Custom Tank – Concentric Chambers, Vertical Flow
Assumed T10/T = 0.7
Standard Design Practice – Well-baffled T10/T = 0.7
Tracer Analysis – 0.38 to 0.51
Recommended T10/T=0.4

## Slide 53: dDIP Follow-up
Provide Lab skills training
Continue to investigate pH methods (utility, research, EPA 150.3, Vendors, water quality labs)
Eliminate color comparator methods (color wheel, strips)
Revise treatment plant report forms
Develop/refine monitoring guidance for systems
Evaluate more site visits (101!)
Explore impact on other programs (LCR, GW disinfection, fluoridation)

## Slide 54: For More Information
JAWWA (Oct 2016)
Englehardt & Malkov, 2015, “Plumbing Sample to a Process Analyzer”, Chlorination, Chloramination and Chlorine Measurement, Appendix C. Hach Company, Loveland.

## Slide 55: THANKS!
Camp Berachah
Doe Bay Community
Kapowsin Water District
Spring Point Homeowner’s Association
Madrona Community
Oyster Creek Inn
McHaven Inc
Olga Water Users Association

## Slide 56: What is Data Integrity?
Maintaining and ensuring accuracy and consistency of data from sample collection point until the data is used.
VERIFY often so we can TRUST our data and so customers will TRUST us!

## Slide 57
Steve Deem, P.E.
253.395.6767
steve.deem@doh.wa.gov
Nancy Feagin, P.E.
253.395.6765
nancy.feagin@doh.wa.gov
Questions? Comments?