## Est. Useful Life - HIDE SHEET (hidden)
For Lookup | Asset Category | Asset Type | Estimated Useful Life
CollectionAsbestos cement (AC) Pipe | Collection | Asbestos cement (AC) Pipe | 50
CollectionAir Release Valve | Collection | Air Release Valve | 10
CollectionBrick Pipe | Collection | Brick Pipe | 50
CollectionCast Iron Pipe | Collection | Cast Iron Pipe | 50
CollectionConcrete Pipe | Collection | Concrete Pipe | 50
CollectionDuctile Iron (DI) Pipe | Collection | Ductile Iron (DI) Pipe | 50
CollectionHDPE Pipe | Collection | HDPE Pipe | 80
CollectionRCP Pipe | Collection | RCP Pipe | 80
CollectionPolyvinyl Chloride (PVC) Pipe | Collection | Polyvinyl Chloride (PVC) Pipe | 80
CollectionSteel Pipe | Collection | Steel Pipe | 50
CollectionVitrified Clay Pipe (VCP) | Collection | Vitrified Clay Pipe (VCP) | 50
CollectionLift Station Structure | Collection | Lift Station Structure | 30
CollectionManhole Riser and Cover | Collection | Manhole Riser and Cover | 25
CollectionOther Pipe | Collection | Other Pipe | 50
Control SystemFlow Meter | Control System | Flow Meter | 15
Control SystemMotor Control Center | Control System | Motor Control Center | 30
Control SystemOther Communication System | Control System | Other Communication System | 10
Control SystemOther Power Supply | Control System | Other Power Supply | 5
Control SystemSCADA | Control System | SCADA | 10
Control SystemTelemetry | Control System | Telemetry | 10
Control SystemValve | Control System | Valve | 20
Control SystemVariable Frequency Drive | Control System | Variable Frequency Drive | 10
Analytical EquipmentAdd details in Asset Description | Analytical Equipment | Add details in Asset Description | 5
OtherBuilding | Other | Building | 50
OtherComputer | Other | Computer | 5
OtherElectrical | Other | Electrical | 20
OtherGenerator | Other | Generator | 20
OtherLab Equipment | Other | Lab Equipment | 5
OtherOther | Other | Other | 10
OtherTools | Other | Tools | 15
OtherVehicle | Other | Vehicle | 10
PumpEffluent | Pump | Effluent | 15
PumpGrinder | Pump | Grinder | 5
PumpMetering/Chemical Feed | Pump | Metering/Chemical Feed | 5
PumpMotor | Pump | Motor | 10
PumpOther | Pump | Other | 15
PumpSeptic Tank Effluent | Pump | Septic Tank Effluent | 15
PumpTransfer | Pump | Transfer | 15
Safety EquipmentAdd details in Asset Description | Safety Equipment | Add details in Asset Description | 5
TreatmentActivated Sludge System | Treatment | Activated Sludge System | 20
TreatmentAeration | Treatment | Aeration | 20
TreatmentBioReactor Membrane | Treatment | BioReactor Membrane | 7
TreatmentBlower | Treatment | Blower | 20
TreatmentChlorination System | Treatment | Chlorination System | 10
TreatmentClarifier | Treatment | Clarifier | 20
TreatmentMixer | Treatment | Mixer | 15
TreatmentConcrete Treatment Basin | Treatment | Concrete Treatment Basin | 50
TreatmentSteel Treatment Basin | Treatment | Steel Treatment Basin | 15
TreatmentDrainfield | Treatment | Drainfield | 15
TreatmentExtended Aeration System | Treatment | Extended Aeration System | 20
TreatmentFilter - Cloth Media | Treatment | Filter - Cloth Media | 30
TreatmentFilter - Sand Media | Treatment | Filter - Sand Media | 15
TreatmentGrit removal | Treatment | Grit removal | 20
TreatmentInfiltration Basin | Treatment | Infiltration Basin | 20
TreatmentLagoon Cover | Treatment | Lagoon Cover | 15
TreatmentLagoon Dike | Treatment | Lagoon Dike | 50
TreatmentLagoon Liner Clay | Treatment | Lagoon Liner Clay | 20
TreatmentLagoon Liner Exposed HDPE, EPDM | Treatment | Lagoon Liner Exposed HDPE, EPDM | 20
TreatmentLagoon Liner Buried HDPE, EPDM, | Treatment | Lagoon Liner Buried HDPE, EPDM, | 80
TreatmentLagoon Liner Buried PVC | Treatment | Lagoon Liner Buried PVC | 20
TreatmentOther | Treatment | Other | 10
TreatmentOutfall | Treatment | Outfall | 20
TreatmentRotating Biological Contactor System | Treatment | Rotating Biological Contactor System | 20
TreatmentSeptic Tank | Treatment | Septic Tank | 20
TreatmentSequencing Batch Reactor Tank | Treatment | Sequencing Batch Reactor Tank | 20
TreatmentSolids Handling | Treatment | Solids Handling | 10
TreatmentTrickling Filter System | Treatment | Trickling Filter System | 20
TreatmentUltraviolet Disinfection | Treatment | Ultraviolet Disinfection | 20
UnknownUnknown | Unknown | Unknown | Undefined

## Weighting Tables - HIDE SHEET (hidden)
Question | Tab(s) | Weight | Calculation | Total Maximum Score
Current Condition | Condition Assessment; Vulnerabiliity Assessment | 1 | Condition Assessment | 5
Reliability | Condition Assessment; Vulnerability Assessment | 1 | Consequence of Failure | 7
Current Status | Condition Assessment | 1 | Probability of Failure | 5
Importance | Vulnerability Assessment | 1
Compliance | Vulnerability Assessment | 1
Estimated Remaining Life | Vulnerability Assessment | 1
Capacity | Vulnerability Assessment | 1
Repair Schedule | Vulnerability Assessment | 1
Redundancy | Critical Assets | 1
Public Health and Environment | Vulnerability Assessment | 2

## Dropdown Menus - HIDE SHEET (hidden)
Asset Category | Asset Product List | Current Condition | Yes/No Questions | Current Status | Capacity | Importance
Collection | Collection Product | Excellent | Yes | Active | At capacity | None
Control System | Control System Product | Good | No | Back-up | Below capacity | Less than 25%
Analytical Equipment | Analytical Equipment Product | Fair | Unknown |  | Beyond capacity | 25-50%
Pump | Pump Product | Poor |  |  |  | 50-75%
Treatment | Treatment Product | Very Poor |  |  |  | Greater than 75%
Safety Equipment | Other Product
Other

## Asset Tables - HIDE SHEET (hidden)
Collection | Control System | Pump | Treatment | Other | Analytical Equipment | Safety Equipment
Asbestos cement (AC) Pipe | Flow Meter | Effluent | Grit removal | Building | Add details in Asset Description | Add details in Asset Description
Polyvinyl Chloride (PVC) Pipe | Motor Control Center | Grinder | Aeration | Computer
Brick Pipe | Other Communication System | Metering/Chemical Feed | Blower | Electrical
Cast Iron Pipe | Other Power Supply | Septic Tank Effluent | Clarifier | Generator
Concrete Pipe | SCADA | Motor | Mixer | Lab Equipment
Ductile Iron (DI) Pipe | Telemetry | Transfer | Concrete Treatment Basin | Other
HDPE Pipe | Valve | Other | Steel Treatment Basin | Tools
RCP Pipe | Variable Frequency Drive |  | Septic Tank | Vehicle
Vitrified Clay Pipe (VCP) |  |  | Filter - Cloth Media
Other Pipe |  |  | Filter - Sand Media
Air Release Valve |  |  | Solids Handling
Lift Station Structure |  |  | Sequencing Batch Reactor Tank
Manhole Riser and Cover |  |  | BioReactor Membrane
Steel Pipe |  |  | Activated Sludge System
Extended Aeration System
Rotating Biological Contactor System
Trickling Filter System
Lagoon Cover
Lagoon Dike
Lagoon Liner Clay
Lagoon Liner Exposed HDPE, EPDM
Lagoon Liner Buried HDPE, EPDM
Lagoon Liner Buried PVC
Chlorination System
Ultraviolet Disinfection
Infiltration Basin
Drainfield
Outfall
Other

## 0a_Basic Information
Small Community Assistance Planning (SCAP) Tool
Wastewater Assets
U.S. Environmental Protection Agency Region 7
Move left to right to ensure the accurate dropdown menus are available for selection. Cells colored Blue contain dropdown menus for selection. Cells colored Red are for manually entering information. Cells colored Yellow are auto-filled, but can be overwritten. Cells colored Gray are for manually entering optional information. Cells colored Green are calculated output values.
FILL IN THE INFORMATION BELOW
Utility Name:
Utility Location:
Date of Inventory:
System Capacity:
Population Served:
Number of Connections:
Assessor Name:
This inventory is for WASTEWATER assets only. Utilities with drinking water assets should complete a separate inventory using the Drinking Water tool.

## 1_Asset Inventory
| INSTRUCTIONS: Enter information in cells, either manually or using dropdown menus. Move left to right to ensure the accurate dropdown menus are available for selection. Cells colored Blue contain dropdown menus for selection. Cells colored Red are for manually entering mandatory information. Cells colored Yellow are auto-filled, but can be overwritten. Cells colored Gray are for manually entering optional information. |  |  |  |  | Additional resources:
Asset Management: A Guide for Water and Wastewater Systems
Asset Management: A Handbook for Small Water Systems
Asset Management for Small Utilities
Sustainable Infrastructure Management Program Learning Environment
Taking Stock of your Small Water System: A Simple Asset Inventory for Very Small Water Systems
| Key Information | [10 empty] | Supplemental Information
ID | Asset Category (select first) | Asset Type | Asset Description | System Area | Asset ID | Estimated Useful Life (in years) | Estimated Installation Date (M/D/YYYY) | Remaining Useful Life (in years) | Location | Comments for Inspection, Rehab, or Repair | Operational | Alternate Asset ID | Size/Capacity | Number/ Length/ Notes | Product Information | Estimated Replacement Cost | Model Name/Number | Serial Number | Column1 | Column2 | Column3
Formulas:
Remaining Useful Life (in years) = IF(ISNUMBER([Estimated Useful Life (in years)]),IF(ISNUMBER([Estimated Installation Date (M/D/YYYY)]),IF(([Estimated Useful Life (in years)]-(INT((TODAY()-[Estimated Installation Date (M/D/YYYY)])/365)))<0,0,[Estimated Useful Life (in years)]-(INT((TODAY()-[Estimated Installation Date (M/D/YYYY)])/365))),""),"")

## 2a_Condition Assessment
| INSTRUCTIONS: Enter information in cells, either manually or using dropdown menus. Cells colored Blue contain dropdown menus for selection. Cells colored Yellow are values from previous sheets and cannot be edited. Cells colored Green are calculated output values. |  |  |  | Additional resources:
Asset Management for Your Water System
Asset Management Manual: A.M. Kan Work! - Section 3 and Appendix A
Condition Assessment Strategies and Protocols for Water and Wastewater Utility Assets - Appendix C
Fundamentals of Asset Management - Slide 15
ID | Asset Category and Type | Asset Description | Remaining Useful Life | Current Condition of Asset | Reliability - Does the asset need frequent repairs in addition to routine maintenance? | Condition Assessment Score (higher score indicates elevated concern)

## 2c_Critical Assets
| INSTRUCTIONS: No selections are required for this sheet. Users should review information here to ensure it is correct. Cells colored Yellow are values from previous sheets and cannot be edited. Cells colored Green are calculated output values. The final outputs of this tool are the Criticality Score, Combined Score, and Rank Columns. | [5 empty] | Additional resources:
Asset Management for Your Water System
Developing Asset Management Plans Using CUPSS
Asset Management: A Guide for Water and Wastewater Systems
Asset Management Manual: A.M. Kan Work! - Section 3 and Appendix A
ID | Asset Category and Type | Asset Description | CoF Score | PoF Score | Redundancy | Condition Assessment Score | Criticality Score (higher number indicates more critical) | Combined Score (higher number indicates more critical) | Rank (ordered from highest priority asset [highest score] to lower priority assets)

## 3a_Product Lists - USER SHEET
Collection Product | Contact Info | Control System Product | Contact Info | Pump Product | Contact Info | Treatment Product | Contact Info
Other Product | Contact Info | Analytical Equipment Product | Contact Info | Safety Equipment Product | Contact Info

## 3b_Additional Resources
Resource | Organization | Description
Asset Management: A Guide for Water and Wastewater Systems | Southwest Environmental Finance Center (formerly the New Mexico Environmental Finance Center) | Guidebook outlining the purpose and core steps of asset management.
Asset Management: A Handbook for Small Water Systems | U.S. Environmental Protection Agency | Step-wise introduction to the principles of asset management, for small community water systems
Asset Management Manual: A.M. Kan Work! | Southwest Environmental Finance Center | Comprehensive asset management and energy efficiency manual for water and wastewater systems, including video clips from water system and community representatives
Asset Management for Small Utilities | Water Environment Research Foundation | Guidelines and worksheets for asset inventories, priority ranking, and asset management plan implementation
Asset Management for Your Water System | West Virginia Department of Health and Human Resources | Guidance documents, worksheet tools, and supplemental resources for developing an asset management plan
Condition Assessment Strategies and Protocols for Water and Wastewater Utility Assets - Appendix C | Water Environment Research Foundation | Guidance on conducting condition assessments for water and wastewater assets
Fundamentals of Asset Management | U.S. Environmental Protection Agency | Ten-module, slide-based training on developing an asset management program
Sustainable Infrastructure Management Program Learning Environment | Water Environment Research Foundation | On-line learning environment and supplemental resources for developing asset management plans
Taking Stock of your Small Water System: A Simple Asset Inventory for Very Small Water Systems | U.S. Environmental Protection Agency | Guide for small water systems on developing a simple asset inventory

## 3c_Condition Rating Guidance
Asset Category | Condition Ratings Guidance
Collection | Number of Pipe Breaks in Past 5 Years: Excellent = 0 breaks per mile; Good = 1 break per mile per year; Fair = 2 breaks per mile per year; Poor = 3-4 breaks per mile per year; Very Poor = >4 breaks per mile per year. CCTV Inspection: Excellent = Clean pipe walls, no illegal connections, no visible leaks or inflow. Good = Minor buildup on pipe walls, no illegal connections, no visible leaks or inflow; Fair = Minor build up on pipe walls, no illegal connections, some minor leaks or inflow; Poor = Moderate build up on pipe walls, no illegal connections, minor to substantial leaks or inflow visible. Very Poor = Any of the following - excessive build up on pipe walls substantially restricting flow, one or more illegal connection, substantial leaks or inflow, one or more breaks in pipe. Manhole Riser and Cover: Excellent = No deficiencies noted on cover or in riser; Good = Minor deficiencies; Fair = Moderate deficiencies; Poor = Considerable deficiencies; Very Poor = Cracks in valve box or damaged cover Lift Station: Excellent = In new or like-new condition, no maintenance needed. Good = In adequate condition with only standard maintenance needed; Fair = Beginning to require more frequent maintenance; Poor = Maintenance required often, equipment often breaks down and affects treatment; Very Poor = Equipment is unreliable, breaking down often and commonly affeting treatment. Air Release Valve: Excellent = No detectable leakage; Good = Minor detectable leakage; Fair = Moderate leakage but servicable; Poor = Considerable leakage, barely servicable; Very Poor = Heavy leakage, not servicable Other things to consider: Pipe condition will be influenced by factors such as installation, manufacturing quality, and presense of air release to allow for off gassing of hydrogen sulfide.
Pump | Motor Hours: Excellent = <1,000 hrs; Good = 10,000-50,00 hrs; Fair = 50,000-100,000 hrs; Poor = 100,000-200,000 hrs; Very Poor = >200,000 hrs Vibrations Detected: Excellent = No unusual vibrations; Good = Minor; Fair = Moderate; Poor = Considerable; Very Poor = Major Temperature: Excellent = No unusual temp; Good = Minimal heat; Fair = Heat detected by hand; Poor = Heat uncomfortable to touch; Very Poor = Too hot to touch. Note: Assessment of temperature and leaking seals will not be possible for submerged pumps. Noise: Excellent = No unusual noise; Good = Slight whine/rattle; Fair = Moderate whine/rattle heard over pump noise; Poor = Loud whine/rattle; Very Poor = Disturbingly loud Leaking Seals: Excellent = No visible signs; Good = Minor leaking seals; Fair = Moderate leaking seals; Poor = Considerate leaking seals; Very Poor = Major leaking seals
Treatment | Fencing and Gate: Excellent = The site is secure; Good = Security devices have minor damage but no unauthorized personnel can enter; Fair = Moderate damage allowing unauthorized persons to enter; Poor = Considerable damage to security devices; Very Poor = No security/site exposed to threat Mechanical Equipment: Excellent = In new or like-new condition, no maintenance needed. Good = In adequate condition with only standard maintenance needed; Fair = Beginning to require more frequent maintenance; Poor = Maintenance required often, equipment often breaks down and affects treatment; Very Poor = Equipment is unreliable, breaking down often and commonly affeting treatment. Concrete Treatment Basin: Excellent = In new or like-new condition, no visible deterioration; Good = In adequate condition, no visible deterioration; Fair = Moderate deterioration, some signs of cracking; Poor = Considerable deterioration and cracking; Very Poor = Major cracks and visible leaks. Steel Treatment Vessel Exterior: Excellent = No chipping or visible thin spots; Good = Minor areas of chipping, rust or thin areas; Fair = Moderate chipping, rust, cracks or thin areas; Poor = Considerable chipping, rust, cracks, or thin areas; Very Poor = Major cracks, thin areas, or visible leaks Lagoon Dike: Excellent = Stable slope, no unwanted vegetation; Good = Some erosion of walls, some unwanted vegetation; Fair = Moderate deterioration of walls and/or unwanted vegetation; Poor = Considerable deterioration of walls and/or unwanted vegetation; Very Poor = Substantial deterioration of walls and/or excessive unwanted vegetation. Lagoon Liner Exposed (UV stable material): Excellent = No visible signs of wear on liner, no leakage noted. Good = Very few signs of wear or traffice but no breakage or leakage noted; Fair = Moderate signs of wear or traffic on liner but no breakage or leakage noted; Poor = Liner has some break through and leakage is noted or likely; Very Poor = Multiple breaks in liner or worn sections. Leakage is noted or likely. Note: Lagoon liner life expectancy will depend on thickness of the liner, adn manufacturer's warranty should be considered in assessing the anticipated life of a specific liner installation. Lagoon Liner Buried: Excellent = No unexposed sections, no leakage noted. Good = Very few minor exposed sections, no leakage noted; Fair = Some exposed sections but no breaks, no leakage noted; Poor = One or more exposed and compromised sections some leakage; Very Poor = Multiple exposed and compromised sections with leakage. Note: Lagoon liner life expectancy will depend on thickness of the liner, adn manufacturer's warranty should be considered in assessing the anticipated life of a specific liner installation. Effluent Quality: Excellent = Continually meets all permit levels; Good = Rarely exceeds one or more permit level; Fair = Occasionally exceeds one or more permit level; Poor = Occasionally exceeds one or more permit level and is out of compliance; Very Poor = Frequently exceeds one or more permit level and is out of compliance Unplanned Outages: Excellent = 0/year; Good = 1/year; Fair = 2/year; Poor = 3/year; Very Poor = >3 per year
Control System | Controls: Excellent = Fully operational, just updated. Good = Minor issues with operability, recently updated; Fair = Moderate issues with operability, updates due; Poor = Considerable issues with operability, updates required and overdue; Very Poor = Substantial issues with operability, updates requried and long overdue. Meter - Years Since Last Calibration: Excellent = <1 year; Good = 1-2 years; Fair = 2-3 years; Poor = 3-4 years; Very Poor = >4 years Valve Operation: Excellent = Easy to operate; Good = Minor resistance to operation; Fair = Moderate resistance to operation; Poor = Very hard to operates; Very Poor = cannot operate valve Other things to consider: Controls operating within manufacturers' recommendations.
Other | Building: Excellent = No deterioratoin of siding, roof, foundation, doors and windows; Good = Some deterioration; Fair = Moderate deterioration; Poor = Considerable deterioration; Very Poor = Substantial deterioration Generator: Excellent = No visible deterioration, fully operable whenever needed. Good = Minor deterioration and/or some difficulty in start up; Fair = Moderate deterioration and/or difficult to start when needed; Poor = Considerable deterioration and/or does not start or remain running as needed; Very Poor = Substantial deterioration and not reliable to start or run as needed. Vehicles: Excellent = No deterioration and runs reliably; Good = Some deterioration but runs reliably. Fair = Moderate deterioration and some engine repair needed; Poor = Considerable deterioration and engine repair needed; Very Poor = Substantial deterioration, engine repair needed, does not run reliably. Other things to consider: Assets operating within manufacturers' recommendations.