## Deposition Mode
| Example of a Daily Membrane Report Template (page 1, raw data and performance summary) | [19 empty] | Example of a Daily Membrane Report Template (page 2, Calculated Values)
| Date |  | CFE | [5 empty] | EP Residual
|  |  | NTU1 (NTU) | NTU2 (NTU) | NTU3 (NTU) | NTU4 (NTU) | NTU5 (NTU) | NTU6 (NTU) | Min | Max Duration (hrs) |  | No. of Modules In Service |  | Surface Area per Module (ft2) |  | Does your SCADA system report it's Temperature readings in degrees Fahrenheit?
|  |  | Unit 1 | [8 empty] | Minimum Required EP Residual
|  |  | Max mNTU | Avg Norm Flux | Avg TMP
TCEQ-Approved DIT Parameters
|  |  | Min Pmin (psi) | Max ΔP/Δt (psi/min) | Successful CA? | [6 empty] | Ptest (psi) |  | UCL (psi/min)
|  | Feed | Unit 1 | [15 empty] | CFE | Entry Point | Unit 1 | [7 empty] | EP | Off-Spec Production
| Date/Time | Turbidity (NTU) | Filtrate to Clearwell? | Filtrate Turbidity (NTU) | Filtrate Flow Rate (gpm) | Water Temp (oC) | Normalized Flux @ 20oC (gpd/ft2) | Feed Pressure (psi) | Filtrate Pressure (psi) | TMP (psi) | Normalized Specific Flux @ 20oC (gpd/ft2-psi) | Most Recent DIT Date & Time | DIT Terminated Prematurely? | Pinitial (psi) | Pmin (psi) | Pfinal (psi) | Test Duration (seconds) | ΔP/Δt (psi/min) | Turbidity (NTU) | CL2 Residual (mg/L) | Filtrate Turbidity Analyses (NTU) | Water Temp (oC) | Normalized Flux (gpd/ft2) | TMP (psi) | Normalized Specific Flux (gpd/ft2-psi) | Pmin (psi) | ΔP/Δt (psi/min) | DIT Passed? | Duration of Low Residual (hrs) | Corrective Action Completed | Continued Production After Failed DIT
* | 0
0.0034722
0.0069444
0.010417
0.013889
0.017361
0.020833
0.024306
0.027778
0.03125
0.034722
0.038194
0.041667
0.045139
0.048611
0.052083
0.055556
0.059028
0.0625
0.065972
0.069444
0.072917
0.076389
0.079861
0.083333
0.086806
0.090278
0.09375
0.097222
0.10069
0.10417
0.10764
0.11111
0.11458
0.11806
0.12153
0.125
0.12847
0.13194
0.13542
0.13889
0.14236
0.14583
0.14931
0.15278
0.15625
0.15972
0.16319
* | 0.16667
0.17014
0.17361
0.17708
0.18056
0.18403
0.1875
0.19097
0.19444
0.19792
0.20139
0.20486
0.20833
0.21181
0.21528
0.21875
0.22222
0.22569
0.22917
0.23264
0.23611
0.23958
0.24306
0.24653
0.25
0.25347
0.25694
0.26042
0.26389
0.26736
0.27083
0.27431
0.27778
0.28125
0.28472
0.28819
0.29167
0.29514
0.29861
0.30208
0.30556
0.30903
0.3125
0.31597
0.31944
0.32292
0.32639
0.32986
* | 0.33333
0.33681
0.34028
0.34375
0.34722
0.35069
0.35417
0.35764
0.36111
0.36458
0.36806
0.37153
0.375
0.37847
0.38194
0.38542
0.38889
0.39236
0.39583
0.39931
0.40278
0.40625
0.40972
0.41319
0.41667
0.42014
0.42361
0.42708
0.43056
0.43403
0.4375
0.44097
0.44444
0.44792
0.45139
0.45486
0.45833
0.46181
0.46528
0.46875
0.47222
0.47569
0.47917
0.48264
0.48611
0.48958
0.49306
0.49653
* | 0.5
0.50347
0.50694
0.51042
0.51389
0.51736
0.52083
0.52431
0.52778
0.53125
0.53472
0.53819
0.54167
0.54514
0.54861
0.55208
0.55556
0.55903
0.5625
0.56597
0.56944
0.57292
0.57639
0.57986
0.58333
0.58681
0.59028
0.59375
0.59722
0.60069
0.60417
0.60764
0.61111
0.61458
0.61806
0.62153
0.625
0.62847
0.63194
0.63542
0.63889
0.64236
0.64583
0.64931
0.65278
0.65625
0.65972
0.66319
* | 0.66667
0.67014
0.67361
0.67708
0.68056
0.68403
0.6875
0.69097
0.69444
0.69792
0.70139
0.70486
0.70833
0.71181
0.71528
0.71875
0.72222
0.72569
0.72917
0.73264
0.73611
0.73958
0.74306
0.74653
0.75
0.75347
0.75694
0.76042
0.76389
0.76736
0.77083
0.77431
0.77778
0.78125
0.78472
0.78819
0.79167
0.79514
0.79861
0.80208
0.80556
0.80903
0.8125
0.81597
0.81944
0.82292
0.82639
0.82986
* | 0.83333
0.83681
0.84028
0.84375
0.84722
0.85069
0.85417
0.85764
0.86111
0.86458
0.86806
0.87153
0.875
0.87847
0.88194
0.88542
0.88889
0.89236
0.89583
0.89931
0.90278
0.90625
0.90972
0.91319
0.91667
0.92014
0.92361
0.92708
0.93056
0.93403
0.9375
0.94097
0.94444
0.94792
0.95139
0.95486
0.95833
0.96181
0.96528
0.96875
0.97222
0.97569
0.97917
0.98264
0.98611
0.98958
0.99306
0.99653
Formulas:
Date = +[Date, row above]+5/1440
WARNING
Do not change the value of any cell or header that is colored blue, dark blue, light blue, sky blue, or any other shade of blue.
Doing so will probably damage the template beyond repair.
WARNING
Do not change the value of any cell or header that is colored blue, dark blue, light blue, sky blue, or any other shade of blue.
Doing so will probably damage the template beyond repair.
Note: See the text box to the right (column AJ) for instructions on how to deal with data that does not reflect actual operating conditions.
WARNING
Do not change the value of any cell or header that is colored blue, dark blue, light blue, sky blue, or any other shade of blue.
Doing so will probably damage the template beyond repair.
Instructions for dealing with data that does not reflect actual operating conditions.
In the event that a recorded value is incorrect because the instrument is being calibrated or has failed and you are recording data by hand, you will need to replace the erroneous values with the grab sample results. Some examples might include:
1) a turbidimeter is being calibrated, cleaned, you are checking its output, etc
2) the CL17 that is monitoring the chlorine residual at the entry point has failed and you are doing grab samples every 4 hours until you fix it.
Steps:
1) be sure you document the situation in the operator log . . . including the beginning and ending time, what is going one (instrument failed, calibration, cleaning, etc) , and what you did to address the issue (such as collecting and analyzing grab samples)
2) wait until the following day so that you don't interfere with XL Reporter or run the risk of missing a real time data point.
3) go to the column that contains the data from the on-line instrument .
4) find the rows that contain the erroneous information (the time row).
5) delete the data in those rows.
6) insert any grab sample results you have in the applicable column and row.
7) save the results to a new file name, like "original name (rev)".
Note on B5: JackSchulzePE: Enter the data that this data was collected. The information entered in this cell will be used to create the 5-minute time stamps shown below.
Note on D5: JackSchulzePE: NTU interval is based on a trailing 4-hour operating interval. For example, NTU1 reading is at midnight and covers the operating period from midnight to 3:55 AM.
Note on D6: JackSchulzePE: NTU1 is the turbidity reading for the time block that begins at midnight and ends at 3:59 AM If you get an "ND" result, it means that the plant was off-line at midnight (the designated sampling time for this time block). Look down column U and find the first data point for the midnight to 3:59 AM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on E6: JackSchulzePE: NTU2 is the turbidity reading for the time block that begins at 4:00 AM and ends at 7:59 AM If you get an "ND" result, it means that the plant was off-line at 4:00 AM (the designated sampling time for this time block). Look down column U and find the first data point for the 4:00 AM to 7:59 AM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on F6: JackSchulzePE: NTU3 is the turbidity reading for the time block that begins at 8:00 AM and ends at 11:59 AM If you get an "ND" result, it means that the plant was off-line at 8:00 AM (the designated sampling time for this time block). Look down column U and find the first data point for the 8:00 AM to 11:59 AM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on G6: JackSchulzePE: NTU4 is the turbidity reading for the time block that begins at noon and ends at 3:59 PM If you get an "ND" result, it means that the plant was off-line at noon (the designated sampling time for this time block). Look down column U and find the first data point for the noon to 3:55 PM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on H6: JackSchulzePE: NTU5 is the turbidity reading for the time block that begins at 4:00 PM and ends at 7:59 PM If you get an "ND" result, it means that the plant was off-line at 4:00 PM (the designated sampling time for this time block). Look down column U and find the first data point for the 4:00 PM to 7:59 PM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on I6: JackSchulzePE: NTU6 is the turbidity reading for the time block that begins at 8:00 p.m. and ends at 11:59 PM If you get an "ND" result, it means that the plant was off-line at 8:00 PM (the designated sampling time for this time block). Look down column U and find the first data point for the 8:00 AM to 11:59 PM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on M6: JackSchulzePE: Enter the number of modules (in this particular unit) that were in operation on the day that this data was collected. This information and the information in cell P6 is used to calculate the total square feet of membrane surface in the unit. This value is used to determine the instantaneous Normalized Flux values that are calculated in column Y.
Note on O6: JackSchulzePE: Enter the number of square feet of membrane surface in each module (in this particular unit). This information and the information in cell N6 is used to calculate the total square feet of membrane surface in the unit. This value is used to determine the instantaneous Normalized Flux values that are calculated in column Y.
Note on Q6: JackSchulzePE: Enter "Yes" if your system reports the temperature readings in oF. Enter "No" if your system reports the temperature readings in oC. You may also use the drop-down list to select your answer. If you leave the cell empty, the template will assume that the values are recorded as degrees Centigrade (or Celsius).
Note on M9: JackSchulzePE: Enter "O.2" if the treated water entering the distribution system was supposed to contained a free chlorine residual (i.e., you are not feeding one of the chemicals used to make chloramines). Enter "O.5" if the treated water entering the distribution system was supposed to contained a monochloramine residual (i.e., you are feeding ammonia, liquid ammonium sulfate, or some other ammoniated chemical to used to create monochloramines). You may also use the drop-down list to select your answer.
Note on D10: JackSchulzePE: If there is no data yet, the cell will be blank. If there are any confirmed (consecutive) readings above 154 mNTU (which are shown in column W), it will capture the highest one. If there is any missing 5-minutes readings (which will be shown in Column W), it will record that there is missing data (MD). If the are no confirmed readings above 154 and no missing data, it will just report the highest reading (from Column W).
Note on E10: JackSchulzePE: If there is no data yet, the cell will be blank. If there are any readings recorded, it will calculate the average of all the values shown in Column X (which are calculated using the TCEQ approved equation).
Note on F10: JackSchulzePE: If there is no data yet, the cell will be blank. If there are any readings recorded, it will calculate the average of all the values shown in Column Y (which are calculated using the TCEQ approved equation).
Note on D12: JackSchulzePE: Minimum test pressure for all the DITs (psi) If one or more DITs were conducted during the day, this will be the lowest minimum pressure value (which are shown in column AA) for any of the tests. If one or more DITs were conducted but no "minimum pressure" data was collected during any of the tests, it will enter an "ND" value because you do not have the required data. If there was no DIT (and all the cells in column AA are blank), the cell will be blank.
Note on E12: JackSchulzePE: Maximum pressure decay rate (psi/min) If one or more DITs were conducted during the day, this will be the highest pressure decay rate (which are shown in column AB) recorded during any of the tests. If one or more DITs were conducted but no "pressure decay rate" data was collected, it will enter an "ND" value because you do not have the required data. If there was no DIT (and all the cells in column AB are blank), the cell will be blank.
Note on F12: JackSchulzePE: Passed the last DIT of the day? A "Yes" value means that the unit failed one or more DITs during the day but did not send any additional water to the clearwell before it passed a subsequent DIT. A "No" value means one of two things. Either: a) the unit failed a DIT during the day but didn't pass the last DIT of the day, or b) the unit failed a DIT and sent additional water to the clearwell before it passed a subsequent DIT. If there was no DIT, the cell will be blank.
Note on M12: JackSchulzePE: Minimum allowable DIT test pressure (psi) Enter the minimum pressure that you must maintain throughout the DIT to pass the test. You can find this information in the TCEQ's most recent DIT Approval Letter for your membrane unit.
Note on O12: JackSchulzePE: Upper Control Limit Enter the maximum pressure decay rate (∆P/∆T) that you can have before you fail your DIT. You can find this information in the TCEQ's most recent DIT Approval Letter for your membrane unit.
Note on B16: JackSchulzePE: The daily membrane unit report should poll (or query) the plant's data bases at defined 5 minute intervals. Although the TCEQ will review and approve other approaches on a case-by-case basis, this one simplifies data management, analysis, and reporting.
Note on D16: JackSchulzePE: This template is designed so that it: 1) can capture instrument readings regardless of whether or not the membrane unit/rack/train is actually sending water to the clearwell (i.e., whether or not it's actually "on-line") but, when determining which data needs to be used to fill out the SWMOR-Alt, 2) will automatically exclude any data recorded at a time when it was not sending water to the clearwell (i.e., was "off-line" because it undergoing a forward flush, backflush/backwash, DIT/MIT, CIP, etc or because it was just not in use and sitting idle). This column is the one the template uses to record the "operational status" of the unit. In this template: 0 = the unit is not sending water to the clearwell (i.e., it was "off-line") and 1 = the unit is sending water to the clearwell (i.e., it was "on-line") The operational status can be based on the position of the effluent/filtrate valve (e.g., the valve is open or the valve is closed), the filtrate flow rate (e.g., filtrate flow rate is > XXX gpm), or some other condition that would indicate the unit is sending filtrate to the clearwell. If you want, you can set up the numeric format for these cells so that a value of 0 will display as "No" and a value of 1 will display as "Yes" (or whatever other format your operators are familiar with)
Note on E16: JackSchulzePE: This column contains the turbidity reading of the water being produced by an individual membrane unit (i.e., the membrane unit's IFE turbidity level in NTUs.) The data in this column is NOT used to complete the SWMOR-Alt. This data point (along with the corresponding data point in column D) is used by column W to determine if the reading was recording at a time that the unit was sending water to the clearwell and by column W to determine if there were confirmed readings above 0.154 NTU. Ultimately, the data in these column W is used to calculate the value shown in Cell D11, which is reported on the SWMOR-Alt. The template automatically determines which IFE data points must be included (and excluded) when determining the result that will to be entered on the SWMOR-Alt. Therefore, the system should record the IFE turbidity reading regardless of the unit's "operational status" (i.e., the "raw" IFE turbidity data for the unit). If your SCADA system records the turbidity readings in mNTUs, you do not have to change your process. However, you will need to change the header to read "mNTU" instead of "NTU" and you will need to eliminate the "NTU to mNTU" conversion factor from the equation in cell D11.
Note on F16: JackSchulzePE: This column contains the instantons flow rate of the water that the individual membrane unit is sending to the clearwell. This data point is used to calculate the instantaneous normalized filter flux that is shown in the correspond cell in column Y. Ultimately, the data in column Y are used calculate the Avg Normalized Flux for the day that is shown in cell E11 and reported on the SWMOR-Alt. The template uses this data point (and the corresponding data point in column D) to automatically determine which normalized flux data points will be included (and excluded) when determining the result that is entered in column Y. Therefore, the system should record the measured filtrate flow rate data for the unit regardless of the unit's "operational status". In some cases, this value is an actual measurement from an IFE flow meter. In other cases, it may be a calculated value based on the feed water flow meter minus some other meter reading. Regardless of how the reading is obtained, it must be the instantaneous filtrate flow rate.
Note on G16: JackSchulzePE: This column contains the temperature of the water. This data point (along with the corresponding data point in column D and the value you enter in cell S6) is used to: 1) determine if the reading was recording at a time that the unit was sending water to the clearwell. 2) determine if the reading needs to be converted from a Fahrenheit value to a Centigrade (or Celsius) value and places the Centigrade reading in the corresponding cell in Column X. and 3) calculate the instantaneous normalized filter flux that is shown in the corresponding cell in column Y. Ultimately, the data in column Y are used calculate the Avg Normalized Flux for the day that is shown in cell E11 and reported on the SWMOR-Alt. The template automatically determines which normalized flux data points will be included (and excluded) when determining the result that is entered in column Y. Therefore, the system should record the measured temperature data for the unit regardless of the unit's "operational status". Some SCADA systems record the temperature reading in degrees Fahrenheit while others use degrees Centigrade (or Celsius). If you report (in cell S6) that you are recording in Fahrenheit, the template will automatically convert your data to Centigrade when it copies the reading to column X, which is the temperature reading used to calculate the instantaneous normalized flux shown in column Y.
Note on H16: JackSchulzePE: This column contains the instantaneous normalized flux that is being recorded by the membrane controller or plant SCADA system. This data is NOT used to complete the SWMOR-Alt. However, you can use it to compare the Normalized Flux values being recorded by the plant system(s) with the corresponding value in column Y. The values in column Y are the ones which are calculated using the TCEQ and EPA approved equations. The column Y values are also the ones used to calculate the Avg Normalized Flux for the day, which is shown in cell E11 and reported on the SWMOR-Alt. If the two values are different, you know that your membrane controller (or SCADA system) is using a proprietary formula to determine the normalized flux. This discrepancy is not necessarily a problem if the vendor is using the proprietary formula to help them diagnose a problem you are having. You just need to be aware that the readings cannot also be used to report data on the SWMOR-Alt.
Note on I16: JackSchulzePE: This column contains the instantaneous pressure reading from the pressure sensor on the feed water line that supplies the membrane unit. This data point (and the corresponding data point in column D) is used to calculate the instantaneous TMP that is shown in the corresponding cell in column Y. Ultimately, the data in column Y are used calculate the Avg TMP for the day, which is shown in cell F11 and reported on the SWMOR-Alt. The template automatically determines which TMP readings will be included (and excluded) when determining the result that needs to be entered on the SWMOR-Alt. Therefore, the system should record the measured pressure data regardless of the unit's "operational status."
Note on J16: JackSchulzePE: This column contains the instantaneous pressure reading from the pressure sensor installed on the filtrate (filter effluent) line. This data point is used to calculate the instantaneous TMP that is shown in the correspond cell in column Z. Ultimately, the values in column Z are used to calculate the Avg TMP for the day, which is shown in cell F11 and reported on the SWMOR-Alt. The template automatically determines which filtrate pressure readings will be included (and excluded) when determining the result that needs to be entered on the SWMOR-Alt. Therefore, the system should record the filtrate pressure regardless of the unit's "operational status."
Note on K16: JackSchulzePE: This column contains the instantaneous TMP value that is being recorded by the membrane controller or plant SCADA system. This data is NOT used to complete the SWMOR-Alt. However, it can be used to compare the TMP values being recorded by the plant system(s) with the corresponding value that are calculated using the TCEQ and EPA approved equations. That value is shown in the correspond cell in column Z. Ultimately, the values in column Z are used to calculate the Avg Normalized Flux for the day, which is the value shown in cell F11 and reported on the SWMOR-Alt.
Note on L16: JackSchulzePE: This column contains the instantaneous normalized specific flux that is being recorded by the membrane controller or plant SCADA system. This data is NOT used to complete the SWMOR-Alt. I only added this column so that you can compare the instantaneous Normalized Specific Flux values calculated by your plant's controller/SCADA system with the corresponding value that's calculated using the "approved" equations (which are shown in the correspond cell in column Z). Note: The only time you should need to do this comparison is if your SCADA system only records the instantaneous Normalized Specific Flux values (but not the instantons Normalized Flux values that would have appeared in column H).
Note on M16: JackSchulzePE: This column contains the date and time stamp of the most recent DIT. The data is used (in conjunction with the instantaneous Pinitial, Pmin, Pfinal, and Test Duration readings) to determine if a new DIT has been conducted since the previous test. Important: The time stamp value can be the time that a DIT was initiated, the time that the DIT ended, or the time that the results were logged. However, all of the data (results) that are associated with a given test (the data that was collected for each individual DIT) must be reported on a single row . . . regardless of what value you use as your time stamp.
Note on N16: JackSchulzePE: This column indicates whether or not the plant was able to collect all of the required data once it started running a DIT procedure. This scenario typically occurs when the membrane controller can reach its target starting pressure but the pressure will not stabilize long enough to begin the data collection process (i.e., start the pressure decay rate timer). In this template: 0 = the system was able to fully execute the DIT and collect all the data required to determine both the minimum pressure and pressure decay rate, and 1 = a DIT was terminated before it completed all the required steps. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell M16.
Note on O16: JackSchulzePE: This column contains the pressure at the beginning of the DIT (i.e., the pressure when pressure decay rate measurements begin at T=0). This data point is used as part of the analysis to: 1) determine the minimum test pressure (Pmin) for the DIT, that is shown in the corresponding cell in column AB, and 2) calculate the pressure decay rate (∆P/∆T) that is shown in the correspond cell in column AC. The values in: • column AB are used to determine the minimum test pressure for all of the DIT's conducted during the day, which is shown in cell D13 and reported on the SWMOR-Alt. • column AC are used to determine the maximum pressure decay rate for all of the DIT's conducted during the day, which is shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell M16.
Note on P16: JackSchulzePE: This column contains the minimum pressure reading recorded at any point during the DIT. Normally, this will be the value recorded at the end of the test (i.e., the pressure when pressure decay rate measurements at T=Ttest). This data is NOT used to complete the SWMOR-Alt. This data point is used: 1) as part of the analysis to determine the minimum test pressure (Pmin) for the DIT, that is shown in the corresponding cell in column AB, and 2) to calculate the pressure decay rate (∆P/∆T) that is shown in the correspond cell in column AC. The values in: • column AB are used to determine the minimum test pressure for all of the DIT's conducted during the day, which is shown in cell D13 and reported on the SWMOR-Alt. • column AC are used to determine the maximum pressure decay rate for all of the DIT's conducted during the day, which is shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell M16.
Note on Q16: JackSchulzePE: This column contains the pressure at the end of the DIT. It will usually be the same value as (Pmin). This data is NOT used to complete the SWMOR-Alt. This data point is used as part of the analysis to: 1) determine the minimum test pressure (Pmin) for the DIT, that is shown in the corresponding cell in column AB, and 2) calculate the pressure decay rate (∆P/∆T) that is shown in the correspond cell in column AC. The values in: • column AB are used to determine the minimum test pressure for all of the DIT's conducted during the day, which is shown in cell D13 and reported on the SWMOR-Alt. • column AC are used to determine the maximum pressure decay rate for all of the DIT's conducted during the day, which is shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell M16.
Note on R16: JackSchulzePE: This column contains the length of time (in seconds) that elapses between the time that the first pressure reading is recorded (Pinitial) and the time the last pressure reading (Pfinal) is recorded. This data point is used to calculate the pressure decay rate (∆P/∆T) that is shown in the correspond cell in column AC. The values in column AC are used to calculate the maximum decay rate for all of the DIT's conducted during the day, which is shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell M16.
Note on S16: JackSchulzePE: This column contains the pressure decay rate that is being recorded by the membrane controller or plant SCADA system. This data is NOT used to complete the SWMOR-Alt. However, it can be used to compare the pressure decay rate values being recorded by the plant system(s) with the corresponding value that are calculated using the TCEQ and EPA approved equations. This value is shown in the corresponding cell in column AC. It is also the one that is ultimately used to calculate the maximum pressure decay rate for all of the DITs conducted during the day, which is the value shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell M16.
Note on T16: JackSchulzePE: This column contains the turbidity readings from the filtrate water produced by all of the membrane units after it has been blended together. Generally, the CFE sample tap location must meet both of the following criteria: 1) the CFE sample tap must be installed at a site that is downstream (after) the point where the water from all the membranes gets mixed together, AND 2) the CFE sample tap must be located upstream (before) the first clearwell that contains the blended filtrate. If your current CFE sample tap does not meet BOTH of those criteria, you need to contact the TCEQ to discuss the situation.
Note on U16: JackSchulzePE: This column contains the disinfectant residual of the water that is entering the distribution system. Generally, this sample tap location must meet both of the following criteria: 1) the EP sample tap must be installed at a site that is downstream of (after) the clearwell that supplies the pump station that sends treated water to the distribution system, AND 2) the EP sample tap must be located downstream of (after) any booster chlorination injection point (i.e., you cannot have the ability to make any further changes to the disinfectant residual after you measure your EP residual). If your current EP sample tap does not meet BOTH of those criteria, you need to contact the TCEQ to discuss the situation.
Note on V16: JackSchulzePE: calculated values This column analyzes the data in columns D and E to identify if there are confirmed readings above 0.154 NTU, if there is missing data, and if there is an unconfirmed reading above 0.154 NTU. The template calculation does 4 things, in the following order: 1) it checks columns D and E for this 5-minute sample and the subsequent 5-minute sample to see if the unit was sending water to the clearwell at both sampling times and, if so, whether both of the two consecutive readings were above 0.154 NTU. If all 4 conditions are met, it records the higher of the two readings. 2) it checks column D to see if the membrane unit was sending water to the clearwell when this 5-min IFE reading was required and, if it was, checks column E to determine if an IFE reading was recorded. If the unit was on-line and the IFE data was not recorded, the template enters "MD" in the cell for this 5-min IFE reading. 3) it runs the column D and E check to see if the unit was on-line and if a turbidity reading was recorded. If it was and the reading was <= 154, it records the value. and 4) it leaves the cell blank if none of the previous 3 conditions exist (which means that one of the two following condition existed at the designated sampling time. a) the unit was off-line (not sending water to the clearwell), or b) there was a single unconfirmed reading above 0.154 NTU (so it should not be included when determining the highest reading.
Note on W16: JackSchulzePE: calculated values This column analyzes the data in cell S6 and columns D and G to determine if the temperature readings are being reported as oC or oF, if the unit was sending water to the clearwell, and if there is missing temperature data. The template calculation does 4 things, in the following order: 1) it checks columns D for this 5-minute sample to see if the unit was sending water to the clearwell and, if not, it leaves the cell blank. 2) if the unit was sending water to the clearwell, it checks column G to determine if the temperature reading was recorded. If the unit was on-line and the temperature data was not recorded, the template enters "MD" in the cell for this 5-min reading. and 3) if the unit was sending water to the clearwell and column G contains a temperature reading, it checks cell S6 to determine if the value is reported as oC or oF. If it is recorded as oF, it converts the value to oC.
Note on X16: JackSchulzePE: calculated values This column contains the 5-minute Normalized Flux readings that are calculated using the TCEQ and EPA approved equations. The data contained in this column is used to used to calculate the Avg Normalized Flux for the day (which is shown in cell E11 and reported on the SWMOR-Alt.) The template calculation does 3 things: 1) it checks column D to see if the membrane unit was "off-line" when the flux data was supposed to be recorded. If it was, it leaves the current cell empty. 2) it checks column F contains flow rate data and column G contains a temperature reading. If either cell is empty, the template reports there is missing data (it records an "MD"). and 3) If columns F and G both contain data, the template uses the TCEQ and EPA approved equation to calculate the instantaneous flux for this 5-minute reading.
Note on Y16: JackSchulzePE: calculated values This column contains the 5-minute TMP readings that are calculated using the TCEQ and EPA approved equations. The data contained in this column is used to used to calculate the Avg TMP for the day (which is shown in cell F11 and reported on the SWMOR-Alt). The template calculation does 3 things: 1) it checks column D to see if the membrane unit was "off-line" when the flux data was supposed to be recorded. If it was, it leaves the current cell empty. 2) it checks columns I, J, and K to determine if any of the three required pressure readings were not recorded, the template enters "MD" in the cell for this 5-min TMP reading. and 3) If columns I, J, and K all contain data, the template calculates the instantaneous TMP for this 5-minute reading.
Note on Z16: JackSchulzePE: calculated values This column contains the calculated instantaneous normalized specific flux that are calculated using the TCEQ and EPA approved equations. This data is NOT used to complete the SWMOR-Alt. The average daily value is calculated by the SWMOR-Alt based on the average normalized flux and TMP values that you report. I only added this column so that you can compare the Normalized Specific Flux values calculated using the "approved" equations with the corresponding value being recorded by the plant's SCADA system (which are shown in the corresponding cell in column L). The only time you should need to do this comparison is if your SCADA system only records the instantaneous Normalized Specific Flux values (but not the instantons Normalized Flux values that would have appeared in column H).
Note on AA16: JackSchulzePE: calculated values This column contains the minimum pressure recorded during a new DIT. The data contained in this column is used to used to calculate the lowest Pmin for the day (which is shown in cell D13 and reported on the SWMOR-Alt. The template calculation does 4 things: 1) it checks column N to see if the time stamp for the last DIT has changed in the last 5 minutes. If it hasn't, it leaves the current cell empty. 2) it checks columns O, P and Q to determine if any of the three required pressure readings were not recorded. If any data is missing, the template enters "ND" in the cell for this DIT. 3) it compares columns O and P and columns O and Q to see if Pmin or Pfinal are greater than Pinitial. If either of those conditions exist, the template enters "ERROR" in the cell for this DIT (since the starting pressure has to be the highest of the three readings.) and 4) it reports the lowest pressure in columns O, P, and Q.
Note on AB16: JackSchulzePE: calculated values This column contains the pressure decay rate recorded during a new DIT. The data contained in this column is used to used to calculate the highest pressure decay rate (∆P/∆T) for the day (which is shown in cell E13 and reported on the SWMOR-Alt. The template calculation does 4 things: 1) it checks column M to see if the time stamp for the "last DIT" has changed in the last 5 minutes. If it hasn't, it leaves the current cell empty. 2) it checks columns O, P, and R to determine if any of the three values (starting pressure, ending pressure, and test duration) are missing. If so, the template enters "ND" in the cell for this DIT. 3) it compares columns O and Q to see if ending pressure is greater than the starting pressure and enters "ERROR" in the cell (since the starting pressure has to be the higher of the two readings.) and 4) it converts the duration from seconds to minutes and calculates the pressure decay rate for the test.
Note on AC16: JackSchulzePE: calculated values This column determines whether or not the unit passed the new DIT. The data contained in this column is used to used to report the worst case DIT results for the day (which is shown in cell F13 and reported on the SWMOR-Alt. The template calculation does 4 things: 1) it checks column M to see if the time stamp for the "last DIT" has changed in the last 5 minutes. If it hasn't, it leaves the current cell empty. 2) it checks column N to determine if the DIT was terminated before it could complete all of the test steps. If so, the template enters "ND" in the cell. 3) it checks to see if columns AA and AB contain numeric values and enters "ND" if either of them do not. and 4) it determines if: a) the value in column AA is greater than or equal to the min required test pressure shown in cell N12, and b) if the value in column AB is lower than or equal to the UCL shown in cell P12. if both conditions are true, then the template enters "Yes" in the cell; otherwise it enters "No."
Note on AD16: JackSchulzePE: calculated values This column contains a running tally of the length of time that the disinfectant residual at the entry point was below minimum requirements. The data contained in this column is used to used to report the maximum duration of a "low residual" event (which is shown in cell K6 and reported on the SWMOR-Alt). The template calculation does 3 things: 1) it checks column U and the previous cell in this column a) If the reading in column U is greater than the required residual shown in cell P9, it leaves this cell blank. b) If there is no reading in column U and the previous cell in this column is not a number, it means that a "low residual event" hasn't begun so it leaves this cell blank (even though column U has no reading) 2) it checks to see if the previous cell in this column is a number (which means that the EP residual had fallen below acceptable levels and there is no data proving it has risen back up to an acceptable level). In this case, it adds 5 minutes to the running tally of the event duration. 3) If neither of the previous conditions apply, it begins a new event timer.

## Cross-Flow Mode
| Example of a Daily Membrane Report Template (page 1, raw data and performance summary) | [20 empty] | Example of a Daily Membrane Report Template (page 2, Calculated Values)
| Date |  | CFE | [5 empty] | EP Residual
|  |  | NTU1 (NTU) | NTU2 (NTU) | NTU3 (NTU) | NTU4 (NTU) | NTU5 (NTU) | NTU6 (NTU) | Min | Max Duration (hrs) |  | No. of Modules In Service |  | Surface Area per Module (ft2) |  | Does your SCADA system report it's Temperature readings in degrees Fahrenheit?
|  |  | Unit 1 | [8 empty] | Minimum Required EP Residual
|  |  | Max mNTU | Avg Norm Flux | Avg TMP
TCEQ-Approved DIT Parameters
|  |  | Min Pmin (psi) | Max ΔP/Δt (psi/min) | Successful CA? | [6 empty] | Ptest (psi) |  | UCL (psi/min)
|  | Feed | Unit 1 | [16 empty] | CFE | Entry Point | Unit 1 | [7 empty] | EP | Off-Spec Production
| Date/Time | Turbidity (NTU) | Filtrate to Clearwell? | Filtrate Turbidity (NTU) | Filtrate Flow Rate (gpm) | Water Temp (oC) | Normalized Flux @ 20oC (gpd/ft2) | Feed Pressure (psi) | Retentate Pressure (psi) | Filtrate Pressure (psi) | TMP (psi) | Normalized Specific Flux @ 20oC (gpd/ft2-psi) | Most Recent DIT Date & Time | DIT Terminated Prematurely? | Pinitial (psi) | Pmin (psi) | Pfinal (psi) | Test Duration (seconds) | ΔP/Δt (psi/min) | Turbidity (NTU) | CL2 Residual (mg/L) | Filtrate Turbidity Analyses (NTU) | Water Temp (oC) | Normalized Flux (gpd/ft2) | TMP (psi) | Normalized Specific Flux (gpd/ft2-psi) | Pmin (psi) | ΔP/Δt (psi/min) | DIT Passed? | Duration of Low Residual (hrs) | Corrective Action Completed | Continued Production After Failed DIT
* | 0
0.0034722
0.0069444
0.010417
0.013889
0.017361
0.020833
0.024306
0.027778
0.03125
0.034722
0.038194
0.041667
0.045139
0.048611
0.052083
0.055556
0.059028
0.0625
0.065972
0.069444
0.072917
0.076389
0.079861
0.083333
0.086806
0.090278
0.09375
0.097222
0.10069
0.10417
0.10764
0.11111
0.11458
0.11806
0.12153
0.125
0.12847
0.13194
0.13542
0.13889
0.14236
0.14583
0.14931
0.15278
0.15625
0.15972
0.16319
* | 0.16667
0.17014
0.17361
0.17708
0.18056
0.18403
0.1875
0.19097
0.19444
0.19792
0.20139
0.20486
0.20833
0.21181
0.21528
0.21875
0.22222
0.22569
0.22917
0.23264
0.23611
0.23958
0.24306
0.24653
0.25
0.25347
0.25694
0.26042
0.26389
0.26736
0.27083
0.27431
0.27778
0.28125
0.28472
0.28819
0.29167
0.29514
0.29861
0.30208
0.30556
0.30903
0.3125
0.31597
0.31944
0.32292
0.32639
0.32986
* | 0.33333
0.33681
0.34028
0.34375
0.34722
0.35069
0.35417
0.35764
0.36111
0.36458
0.36806
0.37153
0.375
0.37847
0.38194
0.38542
0.38889
0.39236
0.39583
0.39931
0.40278
0.40625
0.40972
0.41319
0.41667
0.42014
0.42361
0.42708
0.43056
0.43403
0.4375
0.44097
0.44444
0.44792
0.45139
0.45486
0.45833
0.46181
0.46528
0.46875
0.47222
0.47569
0.47917
0.48264
0.48611
0.48958
0.49306
0.49653
* | 0.5
0.50347
0.50694
0.51042
0.51389
0.51736
0.52083
0.52431
0.52778
0.53125
0.53472
0.53819
0.54167
0.54514
0.54861
0.55208
0.55556
0.55903
0.5625
0.56597
0.56944
0.57292
0.57639
0.57986
0.58333
0.58681
0.59028
0.59375
0.59722
0.60069
0.60417
0.60764
0.61111
0.61458
0.61806
0.62153
0.625
0.62847
0.63194
0.63542
0.63889
0.64236
0.64583
0.64931
0.65278
0.65625
0.65972
0.66319
* | 0.66667
0.67014
0.67361
0.67708
0.68056
0.68403
0.6875
0.69097
0.69444
0.69792
0.70139
0.70486
0.70833
0.71181
0.71528
0.71875
0.72222
0.72569
0.72917
0.73264
0.73611
0.73958
0.74306
0.74653
0.75
0.75347
0.75694
0.76042
0.76389
0.76736
0.77083
0.77431
0.77778
0.78125
0.78472
0.78819
0.79167
0.79514
0.79861
0.80208
0.80556
0.80903
0.8125
0.81597
0.81944
0.82292
0.82639
0.82986
* | 0.83333
0.83681
0.84028
0.84375
0.84722
0.85069
0.85417
0.85764
0.86111
0.86458
0.86806
0.87153
0.875
0.87847
0.88194
0.88542
0.88889
0.89236
0.89583
0.89931
0.90278
0.90625
0.90972
0.91319
0.91667
0.92014
0.92361
0.92708
0.93056
0.93403
0.9375
0.94097
0.94444
0.94792
0.95139
0.95486
0.95833
0.96181
0.96528
0.96875
0.97222
0.97569
0.97917
0.98264
0.98611
0.98958
0.99306
0.99653
Formulas:
Date = +[Date, row above]+5/1440
WARNING
Do not change the value of any cell or header that is colored blue, dark blue, light blue, sky blue, or any other shade of blue.
Doing so will probably damage the template beyond repair.
WARNING
Do not change the value of any cell or header that is colored blue, dark blue, light blue, sky blue, or any other shade of blue.
Doing so will probably damage the template beyond repair.
Note: See the text box to the right (column AK) for instructions on how to deal with data that does not reflect actual operating conditions.
WARNING
Do not change the value of any cell or header that is colored blue, dark blue, light blue, sky blue, or any other shade of blue.
Doing so will probably damage the template beyond repair.
Instructions for dealing with data that does not reflect actual operating conditions.
In the event that a recorded value is incorrect because the instrument is being calibrated or has failed and you are recording data by hand, you will need to replace the erroneous values with the grab sample results. Some examples might include:
1) a turbidimeter is being calibrated, cleaned, you are checking its output, etc
2) the CL17 that is monitoring the chlorine residual at the entry point has failed and you are doing grab samples every 4 hours until you fix it.
Steps:
1) be sure you document the situation in the operator log . . . including the beginning and ending time, what is going one (instrument failed, calibration, cleaning, etc) , and what you did to address the issue (such as collecting and analyzing grab samples)
2) wait until the following day so that you don't interfere with XL Reporter or run the risk of missing a real time data point.
3) go to the column that contains the data from the on-line instrument .
4) find the rows that contain the erroneous information (the time row).
5) delete the data in those rows.
6) insert any grab sample results you have in the applicable column and row.
7) save the results to a new file name, like "original name (rev)".
Note on B5: JackSchulzePE: Enter the data that this data was collected. The information entered in this cell will be used to create the 5-minute time stamps shown below.
Note on D5: JackSchulzePE: NTU interval is based on a trailing 4-hour operating interval. For example, NTU1 reading is at midnight and covers the operating period from midnight to 3:55 AM.
Note on D6: JackSchulzePE: NTU1 is the turbidity reading for the time block that begins at midnight and ends at 3:59 AM If you get an "ND" result, it means that the plant was off-line at midnight (the designated sampling time for this time block). Look down column U and find the first data point for the midnight to 3:59 AM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on E6: JackSchulzePE: NTU2 is the turbidity reading for the time block that begins at 4:00 AM and ends at 7:59 AM If you get an "ND" result, it means that the plant was off-line at 4:00 AM (the designated sampling time for this time block). Look down column U and find the first data point for the 4:00 AM to 7:59 AM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on F6: JackSchulzePE: NTU3 is the turbidity reading for the time block that begins at 8:00 AM and ends at 11:59 AM If you get an "ND" result, it means that the plant was off-line at 8:00 AM (the designated sampling time for this time block). Look down column U and find the first data point for the 8:00 AM to 11:59 AM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on G6: JackSchulzePE: NTU4 is the turbidity reading for the time block that begins at noon and ends at 3:59 PM If you get an "ND" result, it means that the plant was off-line at noon (the designated sampling time for this time block). Look down column U and find the first data point for the noon to 3:55 PM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on H6: JackSchulzePE: NTU5 is the turbidity reading for the time block that begins at 4:00 PM and ends at 7:59 PM If you get an "ND" result, it means that the plant was off-line at 4:00 PM (the designated sampling time for this time block). Look down column U and find the first data point for the 4:00 PM to 7:59 PM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on I6: JackSchulzePE: NTU6 is the turbidity reading for the time block that begins at 8:00 p.m. and ends at 11:59 PM If you get an "ND" result, it means that the plant was off-line at 8:00 PM (the designated sampling time for this time block). Look down column U and find the first data point for the 8:00 AM to 11:59 PM time block and report that value on SWMOR. Note: the beginning of each 4-hour block is marked with an asterisk in column A.
Note on M6: JackSchulzePE: Enter the number of modules (in this particular unit) that were in operation on the day that this data was collected. This information and the information in cell P6 is used to calculate the total square feet of membrane surface in the unit. This value is used to determine the instantaneous Normalized Flux values that are calculated in column Y.
Note on O6: JackSchulzePE: Enter the number of square feet of membrane surface in each module (in this particular unit). This information and the information in cell N6 is used to calculate the total square feet of membrane surface in the unit. This value is used to determine the instantaneous Normalized Flux values that are calculated in column Y.
Note on Q6: JackSchulzePE: Enter "Yes" if your system reports the temperature readings in oF. Enter "No" if your system reports the temperature readings in oC. You may also use the drop-down list to select your answer. If you leave the cell empty, the template will assume that the values are recorded as degrees Centigrade (or Celsius).
Note on M9: JackSchulzePE: Enter "O.2" if the treated water entering the distribution system was supposed to contained a free chlorine residual (i.e., you are not feeding one of the chemicals used to make chloramines). Enter "O.5" if the treated water entering the distribution system was supposed to contained a monochloramine residual (i.e., you are feeding ammonia, liquid ammonium sulfate, or some other ammoniated chemical to used to create monochloramines). You may also use the drop-down list to select your answer.
Note on D10: JackSchulzePE: If there is no data yet, the cell will be blank. If there are any confirmed (consecutive) readings above 154 mNTU (which are shown in column W), it will capture the highest one. If there is any missing 5-minutes readings (which will be shown in Column W), it will record that there is missing data (MD). If the are no confirmed readings above 154 and no missing data, it will just report the highest reading (from Column W).
Note on E10: JackSchulzePE: If there is no data yet, the cell will be blank. If there are any readings recorded, it will calculate the average of all the values shown in Column X (which are calculated using the TCEQ approved equation).
Note on F10: JackSchulzePE: If there is no data yet, the cell will be blank. If there are any readings recorded, it will calculate the average of all the values shown in Column Y (which are calculated using the TCEQ approved equation).
Note on D12: JackSchulzePE: Minimum test pressure for all the DITs (psi) If one or more DITs were conducted during the day, this will be the lowest minimum pressure value (which are shown in column AB) for any of the tests. If one or more DITs were conducted but no "minimum pressure" data was collected during any of the tests, it will enter an "ND" value because you do not have the required data. If there was no DIT (and all the cells in column AB are blank), the cell will be blank.
Note on E12: JackSchulzePE: Maximum pressure decay rate (psi/min) If one or more DITs were conducted during the day, this will be the highest pressure decay rate (which are shown in column AC recorded during any of the tests. If one or more DITs were conducted but no "pressure decay rate" data was collected, it will enter an "ND" value because you do not have the required data. If there was no DIT (and all the cells in column AC are blank), the cell will be blank
Note on F12: JackSchulzePE: Passed the last DIT of the day? A "Yes" value means that the unit failed one or more DITs during the day but did not send any additional water to the clearwell before it passed a subsequent DIT. A "No" value means one of two things. Either: a) the unit failed a DIT during the day but didn't pass the last DIT of the day, or b) the unit failed a DIT and sent additional water to the clearwell before it passed a subsequent DIT. If there was no DIT, the cell will be blank.
Note on M12: JackSchulzePE: Minimum allowable DIT test pressure (psi) Enter the minimum pressure that you must maintain throughout the DIT to pass the test. You can find this information in the TCEQ's most recent DIT Approval Letter for your membrane unit.
Note on O12: JackSchulzePE: Upper Control Limit Enter the maximum pressure decay rate (∆P/∆T) that you can have before you fail your DIT. You can find this information in the TCEQ's most recent DIT Approval Letter for your membrane unit.
Note on B16: JackSchulzePE: The daily membrane unit report should poll (or query) the plant's data bases at defined 5 minute intervals. Although the TCEQ will review and approve other approaches on a case-by-case basis, this one simplifies data management, analysis, and reporting.
Note on D16: JackSchulzePE: This template is designed so that it: 1) can capture instrument readings regardless of whether or not the membrane unit/rack/train is actually sending water to the clearwell (i.e., whether or not it's actually "on-line") but, when determining which data needs to be used to fill out the SWMOR-Alt, 2) will automatically exclude any data recorded at a time when it was not sending water to the clearwell (i.e., was "off-line" because it undergoing a forward flush, backflush/backwash, DIT/MIT, CIP, etc or because it was just not in use and sitting idle). This column is the one the template uses to record the "operational status" of the unit. In this template: 0 = the unit is not sending water to the clearwell (i.e., it was "off-line") and 1 = the unit is sending water to the clearwell (i.e., it was "on-line") The operational status can be based on the position of the effluent/filtrate valve (e.g., the valve is open or the valve is closed), the filtrate flow rate (e.g., filtrate flow rate is > XXX gpm), or some other condition that would indicate the unit is sending filtrate to the clearwell. If you want, you can set up the numeric format for these cells so that a value of 0 will display as "No" and a value of 1 will display as "Yes" (or whatever other format your operators are familiar with)
Note on E16: JackSchulzePE: This column contains the turbidity reading of the water being produced by an individual membrane unit (i.e., the membrane unit's IFE turbidity level in NTUs.) The data in this column is NOT used to complete the SWMOR-Alt. This data point (along with the corresponding data point in column D) is used by column W to determine if the reading was recording at a time that the unit was sending water to the clearwell and by column W to determine if there were confirmed readings above 0.154 NTU. Ultimately, the data in these column W is used to calculate the value shown in Cell D11, which is reported on the SWMOR-Alt. The template automatically determines which IFE data points must be included (and excluded) when determining the result that will to be entered on the SWMOR-Alt. Therefore, the system should record the IFE turbidity reading regardless of the unit's "operational status" (i.e., the "raw" IFE turbidity data for the unit). If your SCADA system records the turbidity readings in mNTUs, you do not have to change your process. However, you will need to change the header to read "mNTU" instead of "NTU" and you will need to eliminate the "NTU to mNTU" conversion factor from the equation in cell D11.
Note on F16: JackSchulzePE: This column contains the instantaneous flow rate of the water that the individual membrane unit is sending to the clearwell. This data point is used to calculate the instantaneous normalized filter flux that is shown in the correspond cell in column Y. Ultimately, the data in column Y are used calculate the Avg Normalized Flux for the day that is shown in cell E11 and reported on the SWMOR-Alt. The template uses this data point (and the corresponding data point in column D) to automatically determine which normalized flux data points will be included (and excluded) when determining the result that is entered in column Y. Therefore, the system should record the measured filtrate flow rate data for the unit regardless of the unit's "operational status". In some cases, this value is an actual measurement from an IFE flow meter. In other cases, it may be a calculated value based on the feed water flow meter minus some other meter reading. Regardless of how the reading is obtained, it must be the instantaneous filtrate flow rate.
Note on G16: JackSchulzePE: This column contains the temperature of the water. This data point (along with the corresponding data point in column D and the value you enter in cell S6) is used to: 1) determine if the reading was recording at a time that the unit was sending water to the clearwell. 2) determine if the reading needs to be converted from a Fahrenheit value to a Centigrade (or Celsius) value and places the Centigrade reading in the corresponding cell in Column X. and 3) calculate the instantaneous normalized filter flux that is shown in the corresponding cell in column Y. Ultimately, the data in column Y are used calculate the Avg Normalized Flux for the day that is shown in cell E11 and reported on the SWMOR-Alt. The template automatically determines which normalized flux data points will be included (and excluded) when determining the result that is entered in column Y. Therefore, the system should record the measured temperature data for the unit regardless of the unit's "operational status". Some SCADA systems record the temperature reading in degrees Fahrenheit while others use degrees Centigrade (or Celsius). If you report (in cell S6) that you are recording in Fahrenheit, the template will automatically convert your data to Centigrade when it copies the reading to column X, which is the temperature reading used to calculate the instantaneous normalized flux shown in column Y.
Note on H16: JackSchulzePE: This column contains the instantaneous normalized flux that is being recorded by the membrane controller or plant SCADA system. This data is NOT used to complete the SWMOR-Alt. However, you can use it to compare the Normalized Flux values being recorded by the plant system(s) with the corresponding value in column Y. The values in column Y are the ones which are calculated using the TCEQ and EPA approved equations. The column Y values are also the ones used to calculate the Avg Normalized Flux for the day, which is shown in cell E11 and reported on the SWMOR-Alt. If the two values are different, you know that your membrane controller (or SCADA system) is using a proprietary formula to determine the normalized flux. This discrepancy is not necessarily a problem if the vendor is using the proprietary formula to help them diagnose a problem you are having. You just need to be aware that the readings cannot also be used to report data on the SWMOR-Alt.
Note on I16: JackSchulzePE: This column contains the instantaneous pressure reading from the pressure sensor on the feed water line that supplies the membrane unit. This data point (and the corresponding data point in column J) is used to calculate the instantaneous TMP that is shown in the corresponding cell in column Z. Ultimately, the data in column Z are used calculate the Avg TMP for the day, which is shown in cell F11 and reported on the SWMOR-Alt. The template automatically determines which TMP readings will be included (and excluded) when determining the result that needs to be entered on the SWMOR-Alt. Therefore, the system should record the measured pressure data regardless of the unit's "operational status." Note: Please read comment in the header for the "Top Feed" Pressure column (column I). It describes the assumptions that the template uses when calculating the instantaneous TMP values (and some of the limitations that these assumptions create).
Note on J16: JackSchulzePE: This column contains the instantaneous pressure reading from the pressure sensor installed on the "retentate" or "recirculation" line (the one that recirculates the excess feed water used to scour the surface of the membrane when it is operating in the cross-flow mode). This data point (and the corresponding data point in column I) is used to calculate the instantaneous TMP that is shown in the corresponding cell in column Z. Ultimately, the data in column Z are used calculate the Avg TMP for the day, which is shown in cell F11 and reported on the SWMOR-Alt. The template automatically determines which TMP readings will be included (and excluded) when determining the result that needs to be entered on the SWMOR-Alt. Therefore, the system should record the measured pressure data regardless of the unit's "operational status."
Note on K16: JackSchulzePE: This column contains the instantaneous pressure reading from the pressure sensor installed on the filtrate (filter effluent) line. This data point is used to calculate the instantaneous TMP that is shown in the correspond cell in column Z. Ultimately, the values in column Z are used to calculate the Avg TMP for the day, which is shown in cell F11 and reported on the SWMOR-Alt. The template automatically determines which filtrate pressure readings will be included (and excluded) when determining the result that needs to be entered on the SWMOR-Alt. Therefore, the system should record the filtrate pressure regardless of the unit's "operational status."
Note on L16: JackSchulzePE: This column contains the instantaneous TMP value that is being recorded by the membrane controller or plant SCADA system. This data is NOT used to complete the SWMOR-Alt. However, it can be used to compare the TMP values being recorded by the plant system(s) with the corresponding value that are calculated using the TCEQ and EPA approved equations. That value is shown in the correspond cell in column Z. Ultimately, the values in column Z are used to calculate the Avg Normalized Flux for the day, which is the value shown in cell F11 and reported on the SWMOR-Alt.
Note on M16: JackSchulzePE: This column contains the instantaneous normalized specific flux that is being recorded by the membrane controller or plant SCADA system. This data is NOT used to complete the SWMOR-Alt. I only added this column so that you can compare the instantaneous Normalized Specific Flux values calculated by your plant's controller/SCADA system with the corresponding value that's calculated using the "approved" equations (which are shown in the correspond cell in column AA). Note: The only time you should need to do this comparison is if your SCADA system only records the instantaneous Normalized Specific Flux values (but not the instantaneous Normalized Flux values that would have appeared in column H).
Note on N16: JackSchulzePE: This column contains the date and time stamp of the most recent DIT. The data is used (in conjunction with the instantaneous Pinitial, Pmin, Pfinal, and Test Duration readings) to determine if a new DIT has been conducted since the previous test. Important: The time stamp value can be the time that a DIT was initiated, the time that the DIT ended, or the time that the results were logged. However, all of the data (results) that are associated with a given test (the data that was collected for each individual DIT) must be reported on a single row . . . regardless of what value you use as your time stamp.
Note on O16: JackSchulzePE: This column indicates whether or not the plant was able to collect all of the required data once it started running a DIT procedure. This scenario typically occurs when the membrane controller can reach its target starting pressure but the pressure will not stabilize long enough to begin the data collection process (i.e., start the pressure decay rate timer). In this template: 0 = the system was able to fully execute the DIT and collect all the data required to determine both the minimum pressure and pressure decay rate, and 1 = a DIT was terminated before it completed all the required steps. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell N16.
Note on P16: JackSchulzePE: This column contains the pressure at the beginning of the DIT (i.e., the pressure when pressure decay rate measurements begin at T=0). This data point is used as part of the analysis to: 1) determine the minimum test pressure (Pmin) for the DIT, that is shown in the corresponding cell in column AB, and 2) calculate the pressure decay rate (∆P/∆T) that is shown in the correspond cell in column AC. The values in: • column AB are used to determine the minimum test pressure for all of the DIT's conducted during the day, which is shown in cell D13 and reported on the SWMOR-Alt. • column AC are used to determine the maximum pressure decay rate for all of the DIT's conducted during the day, which is shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell N16.
Note on Q16: JackSchulzePE: This column contains the minimum pressure reading recorded at any point during the DIT. Normally, this will be the value recorded at the end of the test (i.e., the pressure when pressure decay rate measurements at T=Ttest). This data is NOT used to complete the SWMOR-Alt. This data point is used: 1) as part of the analysis to determine the minimum test pressure (Pmin) for the DIT, that is shown in the corresponding cell in column AB, and 2) to calculate the pressure decay rate (∆P/∆T) that is shown in the correspond cell in column AC. The values in: • column AB are used to determine the minimum test pressure for all of the DIT's conducted during the day, which is shown in cell D13 and reported on the SWMOR-Alt. • column AC are used to determine the maximum pressure decay rate for all of the DIT's conducted during the day, which is shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell N16.
Note on R16: JackSchulzePE: This column contains the pressure at the end of the DIT. It will usually be the same value as (Pmin). This data is NOT used to complete the SWMOR-Alt. This data point is used as part of the analysis to: 1) determine the minimum test pressure (Pmin) for the DIT, that is shown in the corresponding cell in column AB, and 2) calculate the pressure decay rate (∆P/∆T) that is shown in the correspond cell in column AC. The values in: • column AB are used to determine the minimum test pressure for all of the DIT's conducted during the day, which is shown in cell D13 and reported on the SWMOR-Alt. • column AC are used to determine the maximum pressure decay rate for all of the DIT's conducted during the day, which is shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell N16.
Note on S16: JackSchulzePE: This column contains the length of time (in seconds) that elapses between the time that the first pressure reading is recorded (Pinitial) and the time the last pressure reading (Pfinal) is recorded. This data point is used to calculate the pressure decay rate (∆P/∆T) that is shown in the correspond cell in column AC. The values in column AC are used to calculate the maximum decay rate for all of the DIT's conducted during the day, which is shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell N16.
Note on T16: JackSchulzePE: This column contains the pressure decay rate that is being recorded by the membrane controller or plant SCADA system. This data is NOT used to complete the SWMOR-Alt. However, it can be used to compare the pressure decay rate values being recorded by the plant system(s) with the corresponding value that are calculated using the TCEQ and EPA approved equations. This value is shown in the corresponding cell in column AC. It is also the one that is ultimately used to calculate the maximum pressure decay rate for all of the DITs conducted during the day, which is the value shown in cell E13 and reported on the SWMOR-Alt. Important: All of the data (results) that was collected for each individual DIT must be reported on a single row. See the comment in cell N16.
Note on U16: JackSchulzePE: This column contains the turbidity readings from the filtrate water produced by all of the membrane units after it has been blended together. Generally, the CFE sample tap location must meet both of the following criteria: 1) the CFE sample tap must be installed at a site that is downstream (after) the point where the water from all the membranes gets mixed together, AND 2) the CFE sample tap must be located upstream (before) the first clearwell that contains the blended filtrate. If your current CFE sample tap does not meet BOTH of those criteria, you need to contact the TCEQ to discuss the situation.
Note on V16: JackSchulzePE: This column contains the disinfectant residual of the water that is entering the distribution system. Generally, this sample tap location must meet both of the following criteria: 1) the EP sample tap must be installed at a site that is downstream of (after) the clearwell that supplies the pump station that sends treated water to the distribution system, AND 2) the EP sample tap must be located downstream of (after) any booster chlorination injection point (i.e., you cannot have the ability to make any further changes to the disinfectant residual after you measure your EP residual). If your current EP sample tap does not meet BOTH of those criteria, you need to contact the TCEQ to discuss the situation.
Note on W16: JackSchulzePE: calculated values This column analyzes the data in columns D and E to identify if there are confirmed readings above 0.154 NTU, if there is missing data, and if there is an unconfirmed reading above 0.154 NTU. The template calculation does 4 things, in the following order: 1) it checks columns D and E for this 5-minute sample and the subsequent 5-minute sample to see if the unit was sending water to the clearwell at both sampling times and, if so, whether both of the two consecutive readings were above 0.154 NTU. If all 4 conditions are met, it records the higher of the two readings. 2) it checks column D to see if the membrane unit was sending water to the clearwell when this 5-min IFE reading was required and, if it was, checks column E to determine if an IFE reading was recorded. If the unit was on-line and the IFE data was not recorded, the template enters "MD" in the cell for this 5-min IFE reading. 3) it runs the column D and E check to see if the unit was on-line and if a turbidity reading was recorded. If it was and the reading was <= 154, it records the value. and 4) it leaves the cell blank if none of the previous 3 conditions exist (which means that one of the two following condition existed at the designated sampling time. a) the unit was off-line (not sending water to the clearwell), or b) there was a single unconfirmed reading above 0.154 NTU (so it should not be included when determining the highest reading.
Note on X16: JackSchulzePE: calculated values This column analyzes the data in cell S6 and columns D and G to determine if the temperature readings are being reported as oC or oF, if the unit was sending water to the clearwell, and if there is missing temperature data. The template calculation does 4 things, in the following order: 1) it checks columns D for this 5-minute sample to see if the unit was sending water to the clearwell and, if not, it leaves the cell blank. 2) if the unit was sending water to the clearwell, it checks column G to determine if the temperature reading was recorded. If the unit was on-line and the temperature data was not recorded, the template enters "MD" in the cell for this 5-min reading. and 3) if the unit was sending water to the clearwell and column G contains a temperature reading, it checks cell S6 to determine if the value is reported as oC or oF. If it is recorded as oF, it converts the value to oC.
Note on Y16: JackSchulzePE: calculated values This column contains the 5-minute Normalized Flux readings that are calculated using the TCEQ and EPA approved equations. The data contained in this column is used to used to calculate the Avg Normalized Flux for the day (which is shown in cell E11 and reported on the SWMOR-Alt.) The template calculation does 3 things: 1) it checks column D to see if the membrane unit was "off-line" when the flux data was supposed to be recorded. If it was, it leaves the current cell empty. 2) it checks column F contains flow rate data and column G contains a temperature reading. If either cell is empty, the template reports there is missing data (it records an "MD"). and 3) If columns F and G both contain data, the template uses the TCEQ and EPA approved equation to calculate the instantaneous flux for this 5-minute reading.
Note on Z16: JackSchulzePE: calculated values This column contains the 5-minute TMP readings that are calculated using the TCEQ and EPA approved equations. The data contained in this column is used to used to calculate the Avg TMP for the day (which is shown in cell F11 and reported on the SWMOR-Alt. The template calculation does 3 things: 1) it checks column D to see if the membrane unit was "off-line" when the flux data was supposed to be recorded. If it was, it leaves the current cell empty. 2) it checks columns I, J, and K to determine if any of the three required pressure readings were not recorded, the template enters "MD" in the cell for this 5-min TMP reading. and 3) If columns I, J, and K all contain data, the template calculates the instantaneous TMP for this 5-minute reading.
Note on AA16: JackSchulzePE: calculated values This column contains the calculated instantaneous normalized specific flux that are calculated using the TCEQ and EPA approved equations. This data is NOT used to complete the SWMOR-Alt. The average daily value is calculated by the SWMOR-Alt based on the average normalized flux and TMP values that you report. I only added this column so that you can compare the Normalized Specific Flux values calculated using the "approved" equations with the corresponding value being recorded by the plant's SCADA system (which are shown in the correspond cell in column M). The only time you should need to do this comparison is if your SCADA system only records the instantaneous Normalized Specific Flux values (but not the instantaneous Normalized Flux values that would have appeared in column H).
Note on AB16: JackSchulzePE: calculated values This column contains the minimum pressure recorded during a new DIT. The data contained in this column is used to used to calculate the lowest Pmin for the day (which is shown in cell D13 and reported on the SWMOR-Alt. The template calculation does 4 things: 1) it checks column N to see if the time stamp for the last DIT has changed in the last 5 minutes. If it hasn't, it leaves the current cell empty. 2) it checks columns P, Q and R to determine if any of the three required pressure readings were not recorded. If any data is missing, the template enters "ND" in the cell for this DIT. 3) it compares columns P and Q and columns P and R to see if Pmin or Pfinal are greater than Pinitial. If either of those conditions exist, the template enters "ERROR" in the cell for this DIT (since the starting pressure has to be the highest of the three readings.) and 4) it reports the lowest pressure in columns P, Q, and R.
Note on AC16: JackSchulzePE: calculated values This column contains the pressure decay rate recorded during a new DIT. The data contained in this column is used to used to calculate the highest pressure decay rate (∆P/∆T) for the day (which is shown in cell E13 and reported on the SWMOR-Alt. The template calculation does 4 things: 1) it checks column N to see if the time stamp for the "last DIT" has changed in the last 5 minutes. If it hasn't, it leaves the current cell empty. 2) it checks columns P, R, and S to determine if any of the three values (starting pressure, ending pressure, and test duration) are missing. If so, the template enters "ND" in the cell for this DIT. 3) it compares columns P and R to see if ending pressure is greater than the starting pressure and enters "ERROR" in the cell (since the starting pressure has to be the higher of the two readings.) and 4) it converts the duration from seconds to minutes and calculates the pressure decay rate for the test.
Note on AD16: JackSchulzePE: calculated values This column determines whether or not the unit passed the new DIT. The data contained in this column is used to used to report the worst case DIT results for the day (which is shown in cell F13 and reported on the SWMOR-Alt. The template calculation does 4 things: 1) it checks column N to see if the time stamp for the "last DIT" has changed in the last 5 minutes. If it hasn't, it leaves the current cell empty. 2) it checks column O to determine if the DIT was terminated before it could complete all of the test steps. If so, the template enters "No" in the cell. 3) it checks to see if columns AA and AB contain numeric values and enters "ND" if either of them do not. and 4) it determines if: a) the value in column AA is greater than or equal to the min required test pressure shown in cell N12, and b) if the value in column AB is lower than or equal to the UCL shown in cell P12. if both conditions are true, then the template enters "Yes" in the cell; otherwise it enters "No."
Note on AE16: JackSchulzePE: calculated values This column contains a running tally of the length of time that the disinfectant residual at the entry point was below minimum requirements. The data contained in this column is used to used to report the maximum duration of a "low residual" event (which is shown in cell K6 and reported on the SWMOR-Alt. The template calculation does 3 things: 1) it checks column V and the previous cell in this column a) If the reading in column V is greater than the required residual shown in cell P9, it leaves this cell blank. b) If there is no reading in column V and the previous cell in this column is not a number, it means that a "low residual event" hasn't begun so it leaves this cell blank (even though column U has no reading) 2) it checks to see if the previous cell in this column is a number (which means that the EP residual had fallen below acceptable levels and there is no data proving it has risen back up to an acceptable level). In this case, it adds 5 minutes to the running tally of the event duration. 3) If neither of the previous conditions apply, it begins a new event timer.